## Slide 1
PWN drinking water distribution

## Slide 2: Production locations
WTP – Princess Juliana
WTP – Jan Lagrand
WTP – Bergen
WTP – Laren (ground water)
Dune infiltration area
WTP – Wim Mensink
WTP – Martien den Blanken (direct surface water treatment)

## Slide 3: Distribution network
Connected distribution regions
Mixing zones

## Slide 4: Transport and distribution pipes
Material | Pipe length (km) | Pipe length (%)
Asbestos cement | 3 960 | 38
PVC | 2 730 | 26
PE | 1 940 | 19
Grey cast iron | 590 | 6
Nodular cast iron | 520 | 5
Concrete | 350 | 3
Steel | 230 | 2
Else | 70 | 1
Total | 10 390 | 100

## Slide 5: Hydraulics
Pressure:
    Maximum 650 kPa at pumping station
  Setpoint 300 kPa in network
  To reach minimum of 200 kPa at 1.16 m3/h at customer
Residence time:
    Minimal ½ day
  Maximum 10 days
  Usually 2-3 days

## Slide 6: Hydraulic model
Synergi

## Slide 7: Leakage
  Non-revenue water ~6%
  ILI = CARL / UARL
  CARL = Current Actual Real Losses [liter/day]
  UARL = Unavoidable Actual Real Losses [liter/day]
  UARL = (18 x length DN+TN [km] + 0.8 x # lateral connections + 25 x length LCN [km]) x pressure [mwk]
  ILI = 0.52

## Slide 8: Monitoring water quality in distribution system
Hardly any online monitoring in distribution network
Tap samples ~4000 per year
    Sampling by accreditated laboratory (Het Waterlaboratorium: HWL)
Hardly any exceedings of health-related parameters

## Slide 9: Brown water issues
Biological unstable water
Cast iron

## Slide 10: Flushing

## Slide 11: Flushing

## Slide 12: So…
The extensive distribution system of PWN…
Has very limited water losses and provides drinking water of good quality…
Although the hydraulics are only partly known…
And has some challenges in coping with brown water at some locations.