## Slide 1: Towards circular water: Upscaling advanced wastewater treatment by ozonation for pharmaceutical control
J. Versteegh, T. van de Pol, M. Spruijt, M. Hoekstra

## Slide 2: Research partners
HHNK, Water Authority North Holland
PWN, Water Supply Company North Holland
PWN Technologies, R&D Drinking Water Technology

## Slide 3: Stakeholders interests research
HHNK: Quality improvement
PWN: Source protection
HHNK & PWN: Wastewater reuse

## Slide 4: Technical requirements
70% OMP degradation over the entire treatment process
Bromate formation must be manageable

## Slide 5: Research objectives
Comparing two ozone injection systems to make better informed design decisions for the full-scale plant at WWTP Wervershoof
Better understanding of ozonation and hands-on experience

## Slide 6: Comparing ozone injection systems
Roturi®
Inline injection
Rotating venturi
No full-scale experience on WWTP effluent
Bubble Column
Conventional system
Proven technology for WWTP effluent (Germany, Switzerland)

## Slide 7: Experimental setup
Roturi® pilot (10 m3/h)
Bubble Column bench scale (6 L)

## Slide 8: Roturi vs Bubble Column (Spiked)
11 Target pharmaceuticals
Detection limit
Spiked matrix (x100)

## Slide 9: Roturi vs Bubble Column (Metformine)
Low reaction rate constant for ozone (KO3)
Requires higher ozone dosage

## Slide 10: Bromate formation: Roturi
High bromate formation

## Slide 11: Bromate formation: bubble column
Relatively low bromate formation

## Slide 12: Conclusions
The Roturi can degrade more OMP with a lower specific ozone dose than the bubble column
The Roturi forms bromate faster at a higher specific ozone dose

## Slide 13: WWTP Wervershoof
Load: 296000 p.e.
Q24: 50000 m3/d
RWF: 7800 m3/h
DWF: 3000 m3/h

## Slide 14: Design of the full-scale ozonation plant WWTP Wervershoof
3 different ozone injection systems
700 m3/h (1/4 of DWF)
Modular design
Expansion possible

## Slide 15: Roturi
Inline injection
Two Roturis
Compact
Contact tank

## Slide 16: Venturi injection
Conventional
https://www.oxidationtech.com/ozone/solubility/venturi-injector-vs-bubble-diffusers.html

## Slide 17: Diffusers
Conventional
Reaction tank
Ozone
Ozone off-gas

## Slide 18: Scaling up!
Digital Twin for advanced process control
Poster presentation at YWP
Q3 - 2022

## Slide 19: Acknowledgements
Ministery of Infrastructure and Water Management
IPMV (STOWA)
Topconsortia for Knowledge & Innovation (TKI)
Joop Kruithof

## Slide 20
+31 6 82 62 01 46
hhnk.nl
j.versteegh@hhnk.nl
linkedin.com/in/jeremyversteegh